## Power Supply Config
|  |  | Project Name: |  |  |  | Standby Hours: |  | 24
|  |  | Project ID: |  |  |  | Alarm Mins: |  | 5
|  |  | Prepared By: |  |  |  | Derating Factor: |  | 1.2
6808 Battery Calculator (SK) |  |  |  | Date: |  |  | Voltage Drop Warning Threshold % :
Version 18.05.29 | [8 empty] | 10
Panel ID: | 6808 |  | Model: | 6808 Add. Fire Alarm Control Panel |  |  | Max NAC Current: |  | 3.0 Amps
Location: |  |  | Volts: | 24 VDC |  |  | Max Panel Current: |  | 6.0 Amps
Ckt.# | Circuit Name | Qty | Current Draw |  | Wire AWG | Ohms Per | Length(ft) | Actual | Volts @ | %Drop
|  |  | Standby | Alarm | & Type | 1000 Ft. | One-Way | Ohms | EOL
6808 | 6808 CTRL Panel | 1 | 0.17 | 0.365 | N/A
SK | Photo, Photo-T, PhotoR |  | 0 | 0
SK | Heat, Heat-HT, ROR |  | 0 | 0
SK | Beam, Beam-T |  | 0 | 0
SK | Duct |  | 0 | 0
SK | Acclimate |  | 0 | 0
SK | FIRE-CO |  | 0 | 0
SK-PHOTO-W | Photo W | 0 | 0 | 0
SK-PHOTO-R-W | Photo-R-W |  | 0 | 0
SK-PHOTO-T-W | Photo-T-W |  | 0 | 0
SK-HEAT-W | Heat-W | 0 | 0 | 0
SK-HEAT-ROR-W | Heat-ROR-W |  | 0 | 0
SK-HEAT-HT-W | Heat-HT-W |  | 0 | 0
SK | Control |  | 0 | 0
SK | Control-6 |  | 0 | 0
SK | RelayMon-2 |  | 0 | 0
SK | Monitor, Minimon |  | 0 | 0
SK | Monitor-2 |  | 0 | 0
SK | Monitor-10 |  | 0 | 0
SK | Pull-SA, Pull-DA |  | 0 | 0
SK | Relay |  | 0 | 0
SK | Relay-6 |  | 0 | 0
SK | Zone |  | 0 | 0
SK | Zone-6 |  | 0 | 0
SK | Isolator Module |  | 0 | 0
B224BI | Isolator Base |  | 0 | 0
B200SR | Sounder Base |  | 0 | 0
B200S | Intelligent Sounder Base |  | 0 | 0
B200SR-LF | Low Freq Sounder Base |  | 0 | 0
B200S-LF | Low Freq Sounder Base |  | 0 | 0
B224RB | Relay Base |  | 0 | 0
RTS151 | Magnetic Remote Test |  | 0 | 0
RTS151KEY | Key Activated Test |  | 0 | 0
RA100Z | Remote LED |  | 0 | 0
6860 | LCD Remote Annunc |  | 0 | 0
5824 | Serial/Parallel Module |  | 0 | 0
5496 | Power Expander |  | 0 | 0
5895XL | Power Expander |  | 0 | 0
5865-4 | LED Annunciator (4G) |  | 0 | 0
5865-3 | LED Annunciator (3G) |  | 0 | 0
5880 | LED Driver Module |  | 0 | 0
5883 | Relay Module |  | 0 | 0
SK-NIC | Network Input Card |  | 0 | 0
SK-FML | Muilti-Mode Fiber Card | 0 | 0 | 0
SK-FSL | Single-Mode Fiber Card | 0 | 0 | 0
NAC #1 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
NAC #2 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
NAC #3 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
NAC #4 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
Total Standby Current (Amps) |  |  | 0.17 | 0 | Total Alarm Current (Amps)
Standby Time In Hours |  |  | 24 | 0.365 | Alarm Time In Minutes / 60 |  | (5 Mins)
Total Standby AH Required |  |  | 4.08 | 0.083333 | Total Alarm AH Required
Total Combined AH Required |  |  | 4.1104 | 0.030417 | Command Shortcuts
Multiply By The Derating Factor |  |  | 1.2
Minimum Battery AmpHours Required |  |  | 4.9325
Note on F24: The SK-Beam-T draws a maximum of 500 mA from auxiliary power only when the test feature is used. This should be considered when determining auxiliary power capacity but not calculated into current requirements for day to day operation.
Note on F25: The SK-Duct housing contains a vacant mount for a SK-Relay (sold separately). Current draw for the SK-Relay is calculated by increasing the SK-Relay row of the calculation sheet.
Note on F34: Auxiliary power standby draw is 1.7 mA per SK-Control module. You will need to add this draw to the auxiliary power you are using.
Note on F35: Auxiliary power standby draw is 8 mA per SK-Control-6 module. You will need to add this draw to the auxiliary power you are using.
Note on F43: Auxiliary power standby draw is 12 mA per SK-Zone module. You will need to add this draw to the auxiliary power you are using.
Note on F44: Auxiliary power standby draw is 50 mA per SK-Zone-6 module. You will need to add this draw to the auxiliary power you are using.
Note on F47: Auxiliary power standby draw is .5 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on F48: Auxiliary power standby draw is .5 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on F49: Auxiliary power standby draw is 1 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on F50: Auxiliary power standby draw is .5 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on G24: The SK-Beam-T draws a maximum of 500 mA from auxiliary power only when the test feature is used. This should be considered when determining auxiliary power capacity but not calculated into current requirements for day to day operation.
Note on G25: The SK-Duct housing contains a vacant mount for a SK-Relay (sold separately). Current draw for the SK-Relay is calculated by increasing the SK-Relay row of the calculation sheet.
Note on G34: Auxiliary power alarm draw is 7 mA per SK-Control module. You will need to add this draw to the auxiliary power you are using.
Note on G35: Auxiliary power alarm draw is 20 mA per SK-Control-6 module. You will need to add this draw to the auxiliary power you are using.
Note on G43: Auxiliary power alarm draw is 90 mA per SK-Zone module. You will need to add this draw to the auxiliary power you are using.
Note on G44: Auxiliary power alarm draw is 270 mA per SK-Zone-6 module. You will need to add this draw to the auxiliary power you are using.
Note on G47: Auxiliary power alarm draw is 35 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on G48: Auxiliary power alarm draw is 35 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on G49: Auxiliary power alarm draw is 125 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on G50: Auxiliary power alarm draw is 140 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
cfg.
cfg.
cfg.
cfg.
Global Project Values:
Configure Circuits
Print Page
cfg.
cfg.
cfg.
cfg.

## Smokes
Device Database
Device Database
Command Shortcuts
Item# | Device / Description | Current Draw In Amperes
|  | Standby | *Alarm
1 | Unused
2 | Gentex GCC24 Horn/Strobe (15cd) | 0 | 0.143
3 | Gentex GCC24 Horn/Strobe (30cd) | 0 | 0.153
4 | Gentex GCC24 Horn/Strobe (75cd) | 0 | 0.27
5 | Gentex GCC24 Horn/Strobe (95cd) | 0 | 0.341
6 | Gentex GCC24 Horn/Strobe (115cd) | 0 | 0.383
7 | Gentex GCC24 Horn/Strobe (150cd) | 0 | 0.477
8 | Gentex GCS24 Strobe (15cd) | 0 | 0.12
9 | Gentex GCS24 Strobe (30cd) | 0 | 0.13
10 | Gentex GCS24 Strobe (75cd) | 0 | 0.247
11 | Gentex GCS24 Strobe (95cd) | 0 | 0.318
12 | Gentex GCS24 Strobe (115cd) | 0 | 0.36
13 | Gentex GCS24 Strobe (150cd) | 0 | 0.454
14 | Gentex GEC324 Horn/Strobe (15cd) | 0 | 0.134
15 | Gentex GEC324 Horn/Strobe (30cd) | 0 | 0.152
16 | Gentex GEC324 Horn/Strobe (60cd) | 0 | 0.193
17 | Gentex GEC324 Horn/Strobe (75cd) | 0 | 0.236
18 | Gentex GEC324 Horn/Strobe (110cd) | 0 | 0.28
19 | Gentex GES324 Strobe (15cd) | 0 | 0.078
20 | Gentex GES324 Strobe (30cd) | 0 | 0.096
21 | Gentex GES324 Strobe (60cd) | 0 | 0.137
22 | Gentex GES324 Strobe (75cd) | 0 | 0.18
23 | Gentex GES324 Strobe (110cd) | 0 | 0.224
24 | Gentex GEC24 Horn/Strobe (15cd) | 0 | 0.133
25 | Gentex GEC24 Horn/Strobe (30cd) | 0 | 0.151
26 | Gentex GEC24 Horn/Strobe (60cd) | 0 | 0.192
27 | Gentex GEC24 Horn/Strobe (75cd) | 0 | 0.235
28 | Gentex GEC24 Horn/Strobe (110cd) | 0 | 0.279
29 | Gentex GEC24 Horn/Strobe (177cd) | 0 | 0.343
30 | Gentex GEH24 Horn | 0 | 0.056
31 | Gentex GES24 Strobe (15cd) | 0 | 0.078
32 | Gentex GES24 Strobe (30cd) | 0 | 0.096
33 | Gentex GES24 Strobe (60cd) | 0 | 0.137
34 | Gentex GES24 Strobe (75cd) | 0 | 0.18
35 | Gentex GES24 Strobe (110cd) | 0 | 0.224
36 | Gentex GES24 Strobe (177cd) | 0 | 0.288
37 | Gentex GX91 Mini-Horn (Continuous) | 0 | 0.015
38 | Gentex GX93 Mini-Horn (Temporal) | 0 | 0.022
39 | Gentex WGE Strobe (75cd) | 0 | 0.18
40 | Gentex WGEC Horn/Strobe (75cd) | 0 | 0.236
41 | Silent Knight end of line relay EOL-1224RLY | 0.015 | 0.015
42 | System Sensor CH Chime | 0 | 0.054
43 | System Sensor CHS Chime/Stobe (15cd) | 0 | 0.07
44 | System Sensor CHS Chime/Stobe (15/75cd) | 0 | 0.081
45 | System Sensor CHS Chime/Strobe (30cd) | 0 | 0.099
46 | System Sensor CHS Chime/Strobe (75cd) | 0 | 0.165
47 | System Sensor CHS Chime/Strobe (95cd) | 0 | 0.189
48 | System Sensor CHS Chime/Strobe (110cd) | 0 | 0.21
49 | System Sensor CHS Chime/Strobe (115cd) | 0 | 0.217
50 | System Sensor HR/HRK/HW Horn | 0 | 0.069
51 | System Sensor MH Mini-Horn | 0 | 0.029
52 | System Sensor P2/PC2 Horn/Strobe (15cd) | 0 | 0.091
53 | System Sensor P2/PC2 Horn/Strobe (15/75cd) | 0 | 0.1
54 | System Sensor P2/PC2 Horn/Strobe (30cd) | 0 | 0.116
55 | System Sensor P2/PC2 Horn/Strobe (75cd) | 0 | 0.176
56 | System Sensor P2/PC2 Horn/Strobe (95cd) | 0 | 0.201
57 | System Sensor P2/PC2 Horn/Strobe (110cd) | 0 | 0.221
58 | System Sensor P2/PC2 Horn/Strobe (115cd) | 0 | 0.229
59 | System Sensor P2/PC2 Horn/Strobe (135cd) | 0 | 0.255
60 | System Sensor P2/PC2 Horn/Strobe (150cd) | 0 | 0.27
61 | System Sensor P2/PC2 Horn/Strobe (177cd) | 0 | 0.302
62 | System Sensor P2/PC2 Horn/Strobe (185cd) | 0 | 0.309
63 | System Sensor S/SC Strobe (15cd) | 0 | 0.066
64 | System Sensor S/SC Strobe (15/75cd) | 0 | 0.077
65 | System Sensor S/SC Strobe (30cd) | 0 | 0.094
66 | System Sensor S/SC Strobe (75cd) | 0 | 0.158
67 | System Sensor S/SC Strobe (95cd) | 0 | 0.181
68 | System Sensor S/SC Strobe (110cd) | 0 | 0.202
69 | System Sensor S/SC Strobe (115cd) | 0 | 0.21
70 | System Sensor S/SC Strobe (135cd) | 0 | 0.228
71 | System Sensor S/SC Strobe (150cd) | 0 | 0.246
72 | System Sensor S/SC Strobe (177cd) | 0 | 0.281
73 | System Sensor S/SC Strobe (185cd) | 0 | 0.286
74 | System Sensor CHL Chime | 0 | 0.015
75 | System Sensor CHSL Wall Chime/Strobe (15cd) | 0 | 0.052
76 | System Sensor CHSL Wall Chime/Strobe (30cd) | 0 | 0.072
77 | System Sensor CHSL Wall Chime/Strobe (75cd) | 0 | 0.117
78 | System Sensor CHSL Wall Chime/Strobe (95cd) | 0 | 0.137
79 | System Sensor CHSL Wall Chime/Strobe (110cd) | 0 | 0.176
80 | System Sensor CHSL Wall Chime/Strobe (135cd) | 0 | 0.206
81 | System Sensor CHSL Wall Chime/Strobe (185cd) | 0 | 0.246
82 | System Sensor CHSCL Ceiling Chime/Strobe (15cd) | 0 | 0.054
83 | System Sensor CHSCL Ceiling Chime/Strobe (30cd) | 0 | 0.077
84 | System Sensor CHSCL Ceiling Chime/Strobe (75cd) | 0 | 0.124
85 | System Sensor CHSCL Ceiling Chime/Strobe (95cd) | 0 | 0.146
86 | System Sensor CHSCL Ceiling Chime/Strobe (115cd) | 0 | 0.173
87 | System Sensor CHSCL Ceiling Chime/Strobe (150cd) | 0 | 0.206
88 | System Sensor CHSCL Ceiling Chime/Strobe (177cd) | 0 | 0.245
89 | System Sensor HL/HGL Horn | 0 | 0.047
90 | System Sensor P2L Wall Horn/Strobe (15 cd) | 0 | 0.073
91 | System Sensor P2L Wall Horn/Strobe (30 cd) | 0 | 0.94
92 | System Sensor P2L Wall Horn/Strobe (75 cd) | 0 | 0.139
93 | System Sensor P2L Wall Horn/Strobe (95 cd) | 0 | 0.16
94 | System Sensor P2L Wall Horn/Strobe (110 cd) | 0 | 0.182
95 | System Sensor P2L Wall Horn/Strobe (135 cd) | 0 | 0.211
96 | System Sensor P2L Wall Horn/Strobe (185 cd) | 0 | 0.262
97 | System Sensor PC2L Ceiling Horn/Strobe (15 cd) | 0 | 0.071
98 | System Sensor PC2L Ceiling Horn/Strobe (30 cd) | 0 | 0.094
99 | System Sensor PC2L Ceiling Horn/Strobe (75 cd) | 0 | 0.147
100 | System Sensor PC2L Ceiling Horn/Strobe (95 cd) | 0 | 0.165
101 | System Sensor PC2L Ceiling Horn/Strobe (115 cd) | 0 | 0.202
102 | System Sensor PC2L Ceiling Horn/Strobe (150 cd) | 0 | 0.23
103 | System Sensor PC2L Ceiling Horn/Strobe (177 cd) | 0 | 0.273
104 | System Sensor SL Wall Strobe (15cd) | 0 | 0.043
105 | System Sensor SL Wall Strobe (30cd) | 0 | 0.063
106 | System Sensor SL Wall Strobe (75cd) | 0 | 0.107
107 | System Sensor SL Wall Strobe (95cd) | 0 | 0.121
108 | System Sensor SL Wall Strobe (110cd) | 0 | 0.148
109 | System Sensor SL Wall Strobe (135cd) | 0 | 0.172
110 | System Sensor SL Wall Strobe (185cd) | 0 | 0.222
111 | System Sensor SCL Ceiling Strobe (15 cd) | 0 | 0.041
112 | System Sensor SCL Ceiling Strobe (30 cd) | 0 | 0.063
113 | System Sensor SCL Ceiling Strobe (75 cd) | 0 | 0.111
114 | System Sensor SCL Ceiling Strobe (95 cd) | 0 | 0.134
115 | System Sensor SCL Ceiling Strobe (115 cd) | 0 | 0.158
116 | System Sensor SCL Ceiling Strobe (150 cd) | 0 | 0.189
117 | System Sensor SCL Ceiling Strobe (177 cd) | 0 | 0.226
118 | System Sensor HR-LF | 0 | 0.153
119 | System Sensor HW-LF | 0 | 0.153
120 | System Sensor P2RH-LF | 0 | 0.337
121 | System Sensor P2WH-LF | 0 | 0.337
122 | Wheelock AH24 Horn | 0 | 0.08
123 | Wheelock AS241575 Horn/Strobe (1575cd) | 0 | 0.201
124 | Wheelock AS24MCW Horn/Strobe (15cd) | 0 | 0.168
125 | Wheelock AS24MCW Horn/Strobe (30cd) | 0 | 0.205
126 | Wheelock AS24MCW Horn/Strobe (75cd) | 0 | 0.28
127 | Wheelock AS24MCW Horn/Strobe (110cd) | 0 | 0.347
128 | Wheelock AS24MCWH Horn/Strobe (135cd) | 0 | 0.435
129 | Wheelock AS24MCWH Horn/Strobe (185cd) | 0 | 0.56
130 | Wheelock AS24MCC Horn/Strobe (15cd) | 0 | 0.175
131 | Wheelock AS24MCC Horn/Strobe (30cd) | 0 | 0.218
132 | Wheelock AS24MCC Horn/Strobe (75cd) | 0 | 0.301
133 | Wheelock AS24MCC Horn/Strobe (95cd) | 0 | 0.365
134 | Wheelock AS24MCCH Horn/Strobe (115cd) | 0 | 0.435
135 | Wheelock AS24MCCH Horn/Strobe (177cd) | 0 | 0.56
136 | Wheelock CH70 Chime | 0 | 0.022
137 | Wheelock CH70241575 Chime/Strobe (1575cd) | 0 | 0.112
138 | Wheelock CH7024MCW Chime/Strobe (15cd) | 0 | 0.082
139 | Wheelock CH7024MCW Chime/Strobe (30cd) | 0 | 0.114
140 | Wheelock CH7024MCW Chime/Strobe (75cd) | 0 | 0.187
141 | Wheelock CH7024MCW Chime/Strobe (110cd) | 0 | 0.242
142 | Wheelock CH7024MCWH Chime/Strobe (135cd) | 0 | 0.322
143 | Wheelock CH7024MCWH Chime/Strobe (185cd) | 0 | 0.442
144 | Wheelock CH90 Chime | 0 | 0.022
145 | Wheelock CH9024MCC Chime/Strobe (15cd) | 0 | 0.087
146 | Wheelock CH9024MCC Chime/Strobe (30cd) | 0 | 0.127
147 | Wheelock CH9024MCC Chime/Strobe (75cd) | 0 | 0.211
148 | Wheelock CH9024MCC Chime/Strobe (95cd) | 0 | 0.271
149 | Wheelock CH9024MCCH Chime/Strobe (115cd) | 0 | 0.322
150 | Wheelock CH9024MCCH Chime/Strobe (177cd) | 0 | 0.442
151 | Wheelock HS24 Horn | 0 | 0.11
152 | Wheelock HS24MCC Horn/Strobe (15cd) | 0 | 0.175
153 | Wheelock HS24MCC Horn/Strobe (30cd) | 0 | 0.215
154 | Wheelock HS24MCC Horn/Strobe (75cd) | 0 | 0.299
155 | Wheelock HS24MCC Horn/Strobe (95cd) | 0 | 0.359
156 | Wheelock HS24MCCH Horn/Strobe (115cd) | 0 | 0.41
157 | Wheelock HS24MCCH Horn/Strobe (177cd) | 0 | 0.53
158 | Wheelock HS4241575W Horn/Strobe (1575cd) | 0 | 0.2
159 | Wheelock HS424MCW Horn/Strobe (15cd) | 0 | 0.17
160 | Wheelock HS424MCW Horn/Strobe (30cd) | 0 | 0.202
161 | Wheelock HS424MCW Horn/Strobe (75cd) | 0 | 0.275
162 | Wheelock HS424MCW Horn/Strobe (110cd) | 0 | 0.33
163 | Wheelock HS424MCWH Horn/Strobe (135cd) | 0 | 0.41
164 | Wheelock HS424MCWH Horn/Strobe (185cd) | 0 | 0.53
165 | Wheelock MT24 Multitone Appliance | 0 | 0.142
166 | Wheelock MT241575 Multitone/Strobe (1575cd) | 0 | 0.232
167 | Wheelock MTWP2475 Multitone/Strobe (180cd) | 0 | 0.28
168 | Wheelock MT24MCW Multitone/Strobe (15cd) | 0 | 0.202
169 | Wheelock MT24MCW Multitone/Strobe (30cd) | 0 | 0.234
170 | Wheelock MT24MCW Multitone/Strobe (75cd) | 0 | 0.307
171 | Wheelock MT24MCW Multitone/Strobe (110cd) | 0 | 0.362
172 | Wheelock NH24 Horn | 0 | 0.044
173 | Wheelock NS241575W Horn/Strobe (1575cd) | 0 | 0.148
174 | Wheelock NS24MCW Horn/Strobe (15cd) | 0 | 0.118
175 | Wheelock NS24MCW Horn/Strobe (30cd) | 0 | 0.151
176 | Wheelock NS24MCW Horn/Strobe (75cd) | 0 | 0.228
177 | Wheelock NS24MCW Horn/Strobe (110cd) | 0 | 0.288
178 | Wheelock NS24MCC Horn/Strobe (15cd) | 0 | 0.126
179 | Wheelock NS24MCC Horn/Strobe (30cd) | 0 | 0.168
180 | Wheelock NS24MCC Horn/Strobe (75cd) | 0 | 0.253
181 | Wheelock NS24MCC Horn/Strobe (95cd) | 0 | 0.319
182 | Wheelock NS24MCCH Horn/Strobe (115cd) | 0 | 0.394
183 | Wheelock NS24MCCH Horn/Strobe (177cd) | 0 | 0.521
184 | Wheelock RSS/RSSP241575W Strobe (1575cd) | 0 | 0.09
185 | Wheelock RSS/RSSP24MCW Strobe (15cd) | 0 | 0.06
186 | Wheelock RSS/RSSP24MCW Strobe (30cd) | 0 | 0.092
187 | Wheelock RSS/RSSP24MCW Strobe (75cd) | 0 | 0.165
188 | Wheelock RSS/RSSP24MCW Strobe (110cd) | 0 | 0.22
189 | Wheelock RSS/RSSP24MCWH Strobe (135cd) | 0 | 0.3
190 | Wheelock RSS/RSSP24MCWH Strobe (185cd) | 0 | 0.42
191 | Wheelock RSS/RSSP24MCC Strobe (15cd) | 0 | 0.065
192 | Wheelock RSS/RSSP24MCC Strobe (30cd) | 0 | 0.105
193 | Wheelock RSS/RSSP24MCC Strobe (75cd) | 0 | 0.189
194 | Wheelock RSS/RSSP24MCC Strobe (95cd) | 0 | 0.249
195 | Wheelock RSS/RSSP24MCCH Strobe (115cd) | 0 | 0.3
196 | Wheelock RSS/RSSP24MCCH Strobe (177cd) | 0 | 0.42
197 | User Defined
198 | User Defined
199 | User Defined
200 | User Defined
201 | User Defined
202 | User Defined
203 | User Defined
204 | User Defined
205 | User Defined
All of the devices shown in this table will appear as choices in the dropdown boxes used to configure each circuit. To add new devices: Scroll down and replace any of the user defined entries with the information of the device you wish to add to the list of choices.
Return To Main
Return To Circuit Configuration
Print Device Database

## Circuit Config
Circuit Configuration
Project Name: | 0 | Project ID: |  | 0 | Alarm Mins:
Prepared By: | 0 | Date: |  | 0 | Voltage Drop Warning Threshold % :
Ckt. Number: | NAC #1 | Panel ID: | 6808
Ckt. Name: | Notification Appl Circuit | Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
0 | Unused | 0 | 0 | 0 | 0 | 1
0 | Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Ckt. Number: | NAC #2 | Panel ID: | 6808
Ckt. Name: | Notification Appl Circuit | Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Ckt. Number: | NAC #3 | Panel ID: | 6808
Ckt. Name: | Notification Appl Circuit | Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Ckt. Number: | NAC #4 | Panel ID: | 6808
Ckt. Name: | Notification Appl Circuit | Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Project Information
Edit Device Database
Edit Device Database
Print Circuits Detail
Edit Device Database
Edit Device Database

## Devices (hidden)
Device Database
Notification Appliance Database
Item# | Device / Description | Current Draw In Amperes
|  | Standby | Alarm
1 | Unused
2 | Gentex GMH-24-X Horn | 0 | 0.038
3 | Gentex GX90-4 Horn | 0 | 0.015
4 | Gentex GX90S-4-15 Horn | 0 | 0.093
5 | Gentex GX90S-4-1575 Horn | 0 | 0.108
6 | Gentex GXS-4-1575 Strobe | 0 | 0.145
7 | Gentex HG124 Horn | 0 | 0.03
8 | Gentex HS24-110 Horn/Strobe | 0 | 0.14
9 | Gentex HS24-15 Horn/Strobe | 0 | 0.077
10 | Gentex HS24-15/75 Horn/Strobe | 0 | 0.087
11 | Gentex HS24-30 Horn/Strobe | 0 | 0.087
12 | Gentex HS24-60 Horn/Strobe | 0 | 0.114
13 | Gentex HS24-75 Horn/Strobe | 0 | 0.116
14 | Gentex SHG24-110 Horn/Strobe | 0 | 0.25
15 | Gentex SHG24-15/75-C Horn/Strobe | 0 | 0.123
16 | Gentex SHG24-15/75-W Horn/Strobe | 0 | 0.123
17 | Gentex SHG24-15/75-Z Horn/Strobe | 0 | 0.123
18 | Gentex SHG24-30 Horn/Strobe | 0 | 0.123
19 | Gentex SHG24-30/75 Horn/Strobe | 0 | 0.172
20 | Gentex SHG24-60 Horn/Strobe | 0 | 0.145
21 | Gentex ST24-110 Strobe | 0 | 0.11
22 | Gentex ST24-15 Strobe | 0 | 0.047
23 | Gentex ST24-15/75 Strobe | 0 | 0.057
24 | Gentex ST24-30 Strobe | 0 | 0.057
25 | Gentex ST24-60 Strobe | 0 | 0.084
26 | Gentex ST24-75 Strobe | 0 | 0.086
27 | Silent Knight end of line relay EOL-1224RLY | 0.015 | 0.015
28 | System Sensor H12/24 Horn | 0 | 0.025
29 | System Sensor P24110 Horn/Strobe | 0 | 0.165
30 | System Sensor P241575 Horn/Strobe | 0 | 0.074
31 | System Sensor P2430 Horn/Strobe | 0 | 0.092
32 | System Sensor P2475 Horn/Strobe | 0 | 0.148
33 | System Sensor S2415 Strobe | 0 | 0.043
34 | System Sensor S241575 Strobe | 0 | 0.049
35 | System Sensor S2430 Strobe | 0 | 0.067
36 | System Sensor S2475 Strobe | 0 | 0.123
37 | System Sensor SS24110 Strobe | 0 | 0.14
38 | Wheelock AMT-24-IS-VFR Strobe Horn | 0 | 0.04
39 | Wheelock AMT-24-LSM-VFR Strobe Horn | 0 | 0.125
40 | Wheelock AS-24110-HFR Strobe Horn | 0 | 0.202
41 | Wheelock AS-241575-VFR Strobe Horn | 0 | 0.102
42 | Wheelock AS-2415-VFR Strobe Horn | 0 | 0.087
43 | Wheelock AS-2430-VFR Strobe Horn | 0 | 0.135
44 | Wheelock AS-2475-VFR Strobe Horn | 0 | 0.156
45 | Wheelock MIZ-24-R Mini-Horn | 0 | 0.012
46 | Wheelock MIZ-24-W Mini-Horn | 0 | 0.012
47 | User Defined
48 | User Defined
49 | User Defined
50 | User Defined
51 | User Defined
52 | User Defined
53 | User Defined
54 | User Defined
55 | User Defined
56 | User Defined
57 | User Defined
58 | User Defined
59 | User Defined
60 | User Defined
61 | User Defined
62 | User Defined
63 | User Defined
64 | User Defined
65 | User Defined
66 | User Defined
67 | User Defined
68 | User Defined
69 | User Defined
70 | User Defined
71 | User Defined
72 | User Defined
73 | User Defined
74 | User Defined
75 | User Defined
76 | User Defined
77 | User Defined
78 | User Defined
79 | User Defined
80 | User Defined
81 | User Defined
82 | User Defined
83 | User Defined
84 | User Defined
85 | User Defined
86 | User Defined
87 | User Defined
88 | User Defined
89 | User Defined
90 | User Defined
91 | User Defined
92 | User Defined
93 | User Defined
94 | User Defined
95 | User Defined
96 | User Defined
97 | User Defined
98 | User Defined
99 | User Defined
100 | User Defined
101 | User Defined
102 | User Defined
103 | User Defined
104 | User Defined
105 | User Defined
106 | User Defined
107 | User Defined
108 | User Defined
109 | User Defined
110 | User Defined
111 | User Defined
112 | User Defined
113 | User Defined
114 | User Defined
115 | User Defined
116 | User Defined
117 | User Defined
118 | User Defined
119 | User Defined
120 | User Defined
121 | User Defined
122 | User Defined
123 | User Defined
124 | User Defined
125 | User Defined
126 | User Defined
127 | User Defined
128 | User Defined
129 | User Defined
130 | User Defined
131 | User Defined
132 | User Defined
133 | User Defined
134 | User Defined
135 | User Defined
136 | User Defined
137 | User Defined
138 | User Defined
139 | User Defined
140 | User Defined
141 | User Defined
142 | User Defined
143 | User Defined
144 | User Defined
145 | User Defined
146 | User Defined
147 | User Defined
148 | User Defined
149 | User Defined
150 | User Defined
All of the devices shown in this table will appear as choices in the dropdown boxes used to configure each NAC circuit. To add new devices: Scroll down and replace any of the user defined entries with the information of the device you wish to add to the list of choices.
Command Shortcuts
Print Device Database
Return To Main
Return To Circuit Configuration

## Data (hidden)
Conductor Properties NEC Chap. 9
Item | Wire Type | Ohms Per 1000 ft.
1 | #12 Solid | 1.59
2 | #12 Stranded | 1.59
3 | #14 Solid | 2.52
4 | #14 Stranded | 2.52
5 | #16 Solid | 4.02
6 | #16 Stranded | 4.02
7 | #18 Solid | 6.39
8 | #18 Stranded | 6.39
Cell Links For The Wire Type Drop Down Boxes Associated With Each 5395
| 5395(1) | 5395(2) | 5395(3) | 5395(4) | 5395(5) | 5395(6) | 5395(7) | 5395(8)
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
1 | Notification Appl Circuit
2 | Aux Power Circuit
3 | Aux Power Circuit
| I/O1 | 1
| I/O2 | 1
| I/O3 | 1
| I/O4 | 1
| I/O5 | 1
| I/O6 | 1