## Invoice
Fire Suppression Services, Inc.
[5 empty] | 3802 South 2300 East | [6 empty] | 1
Salt Lake City, Utah 84109-3421
Contractor License No. 92-252208-5501
801.277.6464 • 800.273.6465 • 801.278.2199 - FAX
[8 empty] | JOB SITE |  |  | DATE | 2013-10-25
BILLING
[9 empty] | McDonald |  |  |  |  | License | BF License
[13 empty] | Tal Gray | 232
[13 empty] | Heath Danger Field | 61931 | 45-01369
| . | [7 empty] | . |  |  |  | Kent
|  | Billing |  | Job Site |  | X | ANNUAL |  | SEMI-ANNUAL | TANK DATE | Cartridge Type | Cartridge Date
PHONE | [6 empty] | QUARTERLY |  | MONTHLY
FAX | [5 empty] | SALESMAN : |  | Kent L Johnson
CONTACT | [5 empty] | LICENSE NUMBER
DIRECT # | [5 empty] | E-MAIL :
|  | MAINTENANCE |  |  | INSTALLATION |  | EXTINGUISHERS |  | EMERGENCY | Mileage One-Way |  | TIME
|  | DRY CHEMICAL SYSTEM |  |  | EMERGENCY LIGHTING |  | STEAM CLEAN |  | REPAIR | Drive Time One-Way
| X | WET SYSTEM |  | X | WATER SPRINKLER |  | ALARMS | X | BACKFLOW | UNIT PRICE | NON TAX | TAXABLE
[10 empty] | 0 | 0 | 0
1 |  | Annual- Wet Fire Sprinkler Inspection | [7 empty] | 0 | 0 | 0
1 |  | Annual- Backflow Inspection (3" inch DC) | [7 empty] | 0 | 0 | 0
1 |  | Annual- Backflow Inspection (2" inch RP) | [7 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
HAZARDOUS MATERIAL DISPOSAL CHARGE | [11 empty] | 0
|  |  | DUE WHEN |  | LAST COMPANY | NUMBER ON PROPERTY |  | 8% MISCELLANEOUS MATERIALS, INSURANCE, ETC. |  |  | 0 | 0
EXTINGUISHER | [7 empty] | CODE |  | SUBTOTAL | 0 | 0
EM / EX LIGHTING | [9 empty] | TRUCK
[10 empty] | Non-Taxable Total |  | 0
HOOD CLEANING | [7 empty] | REFILE |  | Taxable Sales |  | 0
[8 empty] | 2014-10-25 |  | SALES TAX |  | 0
FILTER CONDITION | [9 empty] | Freight |  | 0
[10 empty] | Handling |  | 0
I, RECEIPT OF COPY: CUSTOMER ACKNOWLEDGES RECEIPT OF COPY AND THAT HE UNDERSTANDS ALL OF THIS AGREEMENT AND PARTICULARLY PARAGRAPHS 1,2,3,4 AND 5 ON THE REVERSE
WHICH SETS FORTH COMPANY'S MAXIMUM LIABILITY. THE SYSTEM'S HAVE BEEN SERVICED IN ACCORDANCE WITH NATIONAL FIRE PROTECTION STANDARDS AND CODES OR CURRENT MFG.
SERVICE REQUIREMENTS AND DOES NOT CERTIFY THE DESIGN AND / OR THE INSTALLATION CRITERIA.
RECEIVED IN GOOD ORDER AND ACCEPTED
Net 15 Days |  |  | WORK AUTHORIZATION NUMBER | [6 empty] | TOTAL |  | 0
PURCHASE / WORK ORDER NUMBER
Cash | [9 empty] | TIMES ARE CORRECT AND JOB COMPLETED SATISFACTORILY
Check |  |  | BY X | [6 empty] | CLAIMS WILL NOT BE HONORED AFTER TEN (10) DAYS FROM DATE
Credit |  |  |  | BUYER SHALL PAY SELLER FOR THIS PURCHASE | [5 empty] | OF SERVICE.
INTEREST WILL BE CHARGED ON OVERDUE ACCOUNTS. 3% PER MONTH | [8 empty] | MINIMUM BILLING OF $35.00
[5 empty] | "THIS INVOICE IS ALSO YOUR STATEMENT" | [6 empty] | THANK YOU

## Watts BF1
Fire Suppression Services, Inc.
3802 South 2300 East
[5 empty] | Salt Lake City, Utah 84109-3421 | [6 empty] | Service # | 19815
[5 empty] | Contractor License No. 92-252208-5501 | [6 empty] | Date | 2013-10-25
801.277.6464 • 800.273.6465 • 801.278.2199 - FAX
BACKFLOW ASSEMBLY TEST FORM | [13 empty] | Type Of
[13 empty] | Protection |  | Assembly
Job Site | [7 empty] | Make | Ames |  |  |  | Zone |  | SVB
[8 empty] | Model | 2000B |  |  |  | Domestic |  | PVB
[8 empty] | Size | 1 1/4" inch |  |  |  | Individual |  | DC | X
[8 empty] | Serial Number | KG-1391 |  |  |  | Containment |  | RP
| Replacement | [11 empty] | Fire Protection | X | DDC
| Existing | X |  |  | Location Of Assembly |  |  | East Back Entry
| New |  |  |  | Assembly Connected To What Equipment | [5 empty] | Fire Sprinkler Riser
| CHECK VALVE #1 |  |  |  | CHECK VALVE #2 |  |  |  | DP RELIEF VALVE |  |  |  | SVB & PVB AIR INLET
INITIAL | PSI Across |  | 1.7 |  | PSI Across |  | 1.7 |  |  | Opened @ |  | PSI |  | Opened @ |  | PSI
TEST
|  |  | Close Tight | X |  |  | Close Tight | X |  |  | Close Tight |  |  |  | Close Tight
[11 empty] | Did Not Open |  |  |  | Did Not Open
|  |  | Leaked |  |  |  | Leaked |  |  |  | Leaked |  |  |  | Leaked
| Parts |  |  |  | Parts |  |  |  | Parts |  |  |  | Parts
| Cleaned |  | Installed |  | Cleaned |  | Installed |  | Cleaned |  | Installed |  | Cleaned |  | Installed
|  | Disk |  |  |  | Disk |  |  |  | Disk Diaphragm |  |  |  | Air Inlet
REPAIRS |  | Spring |  |  |  | Spring |  |  |  | Spring |  |  |  | Disk
|  | Guide |  |  |  | Guide |  |  |  | Guide |  |  |  | Air Inlet
|  | Seat |  |  |  | Seat |  |  |  | Seat |  |  |  | Spring
|  | O-Rings |  |  |  | O-Rings |  |  |  | O-Rings
|  | All Parts |  |  |  | All Parts |  |  |  | All Parts |  |  |  | All Parts
|  | OTHER |  |  |  | OTHER |  |  |  | OTHER |  |  |  | OTHER
| Describe: |  |  |  | Describe: |  |  |  | Describe: |  |  |  | Describe:
FINAL | PSI Across |  | 1.7 |  | PSI Across |  | 1.7 |  |  | Opened @ |  | PSI |  | Opened @ |  | PSI
TEST
|  |  | Close Tight | X |  |  | Close Tight | X |  |  | Close Tight |  |  |  | Close Tight
[11 empty] | Did Not Open |  |  |  | Did Not Open
|  |  | Leaked |  |  |  | Leaked |  |  |  | Leaked |  |  |  | Leaked
| Assembly |  |  | Passed Date : | 2013-10-25 | [5 empty] | Failed Date :
Comments:
| Initial Test By : | Heath Dangerfield | [6 empty] | Final Test By :
| Repaired By : |  |  |  |  | Date :
TEST KIT INFORMATION
|  | Make Of The Test Kit | Mid-West Instrument | [7 empty] | Back Flow
|  | Model : | 845 | [7 empty] | Inspectors Signature : | Heath Dangerfield
|  | Serial Number : | 05081169 | [7 empty] | Ut. Inspectors Number : | #08065
|  | Calibration Date : | 2013-06-07 | [7 empty] | Inspectors Number : | #45-01369
I Certify the above has been performed and I am aware of the final performance
Heath
TEST KIT INFORMATION
|  | Make Of The Test Kit | Mid-West Instrument
|  | Model : | 845
|  | Serial Number : | 05081169
|  | Calibration Date : | 2013-06-07
|  | Inspectors Number : |  | 45-01369
Lucas Montoya
TEST KIT INFORMATION
|  | Make Of The Test Kit | Mid-West Instrument
|  | Model : | 845
|  | Serial Number : | 08061431
|  | Calibration Date : | 2006-10-10
|  | Inspectors Number : |  | 45-01092

## Watts BF1 (2)
Fire Suppression Services, Inc.
3802 South 2300 East
[5 empty] | Salt Lake City, Utah 84109-3421 | [6 empty] | Service # | 19592
[5 empty] | Contractor License No. 92-252208-5501 | [6 empty] | Date | 2013-10-25
801.277.6464 • 800.273.6465 • 801.278.2199 - FAX
BACKFLOW ASSEMBLY TEST FORM | [13 empty] | Type Of
[13 empty] | Protection |  | Assembly
Job Site | [7 empty] | Make | Wilkins |  |  |  | Zone |  | SVB
[8 empty] | Model | 375XL |  |  |  | Domestic |  | PVB
[8 empty] | Size | 2" inch |  |  |  | Individual |  | DC
[8 empty] | Serial Number | A149442 |  |  |  | Containment |  | RP | X
| Replacement | [11 empty] | Fire Protection | X | DDC
| Existing | X |  |  | Location Of Assembly |  |  | East Back Entry
| New |  |  |  | Assembly Connected To What Equipment | [5 empty] | Domestic Water
| CHECK VALVE #1 |  |  |  | CHECK VALVE #2 |  |  |  | DP RELIEF VALVE |  |  |  | SVB & PVB AIR INLET
INITIAL | PSI Across |  | 8.1 |  | PSI Across |  | Okay |  |  | Opened @ | 2.2 | PSI |  | Opened @ |  | PSI
TEST
|  |  | Close Tight | X |  |  | Close Tight | X |  |  | Close Tight | X |  |  | Close Tight
[11 empty] | Did Not Open |  |  |  | Did Not Open
|  |  | Leaked |  |  |  | Leaked |  |  |  | Leaked |  |  |  | Leaked
| Parts |  |  |  | Parts |  |  |  | Parts |  |  |  | Parts
| Cleaned |  | Installed |  | Cleaned |  | Installed |  | Cleaned |  | Installed |  | Cleaned |  | Installed
|  | Disk |  |  |  | Disk |  |  |  | Disk Diaphragm |  |  |  | Air Inlet
REPAIRS |  | Spring |  |  |  | Spring |  |  |  | Spring |  |  |  | Disk
|  | Guide |  |  |  | Guide |  |  |  | Guide |  |  |  | Air Inlet
|  | Seat |  |  |  | Seat |  |  |  | Seat |  |  |  | Spring
|  | O-Rings |  |  |  | O-Rings |  |  |  | O-Rings
|  | All Parts |  |  |  | All Parts |  |  |  | All Parts |  |  |  | All Parts
|  | OTHER |  |  |  | OTHER |  |  |  | OTHER |  |  |  | OTHER
| Describe: |  |  |  | Describe: |  |  |  | Describe: |  |  |  | Describe:
FINAL | PSI Across |  | 8.1 |  | PSI Across |  | Okay |  |  | Opened @ | 2.2 | PSI |  | Opened @ |  | PSI
TEST
|  |  | Close Tight | X |  |  | Close Tight | X |  |  | Close Tight | X |  |  | Close Tight
[11 empty] | Did Not Open |  |  |  | Did Not Open
|  |  | Leaked |  |  |  | Leaked |  |  |  | Leaked |  |  |  | Leaked
| Assembly |  |  | Passed Date : | 2013-10-25 | [5 empty] | Failed Date :
Comments:
| Initial Test By : | Heath Dangerfield | [6 empty] | Final Test By :
| Repaired By : |  |  |  |  | Date :
TEST KIT INFORMATION
|  | Make Of The Test Kit | Mid-West Instrument | [7 empty] | Back Flow
|  | Model : | 845 | [7 empty] | Inspectors Signature : | Heath Dangerfield
|  | Serial Number : | 05081169 | [7 empty] | Ut. Inspectors Number : | #08065
|  | Calibration Date : | 2013-06-07 | [7 empty] | Inspectors Number : | #45-01369
I Certify the above has been performed and I am aware of the final performance
Heath
TEST KIT INFORMATION
|  | Make Of The Test Kit | Mid-West Instrument
|  | Model : | 845
|  | Serial Number : | 05081169
|  | Calibration Date : | 2013-06-07
|  | Inspectors Number : |  | 45-01369
Lucas Montoya
TEST KIT INFORMATION
|  | Make Of The Test Kit | Mid-West Instrument
|  | Model : | 845
|  | Serial Number : | 08061431
|  | Calibration Date : | 2006-10-10
|  | Inspectors Number : |  | 45-01092

## Water Rep
Fire Suppression Services, Inc.
3802 South 2300 East
Salt Lake City, Utah 84109-3421
Contractor License No. 92-252208-5501
801.277.6464 • 800.273.6465 • 801.278.2199 - FAX
Mail Report To: | [5 empty] | Date: | 2013-10-25
Location:
[6 empty] | Inspector: | Heath Dangerfield
Contact on Job:
1. GENERAL | [7 empty] | YES | N/A | NO
a. Is the building occupied?……………………………………………………………………………………………… | [7 empty] | X
b. Are all systems in service?…………………………………………………………………………………………….. | [7 empty] | X
c. Is there a minimum of 18" clearance between the top of storage and the sprinkler defect?……………………. | [7 empty] | X
d. In areas protected by wet system, does the building appear to be properly heated in all areas, including
blind spaces, attics, and perimeter areas, where accessible?…………………………………………………….. | [7 empty] | X
e. Do all exterior openings appear to be protected against freezing?………………………………………………… | [7 empty] | X
f. Does the hand hose on the sprinkler system appear to be satisfactory?…………………………………. | [8 empty] | X
g. Could the owner provide copies of as-built drawings?............................................................................... | [9 empty] | X
h. Is hydraulic data placard in place?……………………………………………………………………………………. | [9 empty] | X
i. When was systems Last 5 year inspection?............................................................................................ __________________ | [7 empty] | 2012-08-09
j. Type of system?................... |  | WET | X | DRY |  | DELUGE
k. Type of inspection?.............. |  | Annual | X | Semi-Annual |  | Quarterly
2. CONTROL VALVES (See Item 14)
a. Are all sprinkler system control valves and all other valves in the appropriate open or closed position?… | [7 empty] | X
b. Are all control valves in the open position and locked or sealed or equipped with a tamper switch?… | [7 empty] | X
c. Were all control valves exercised?……………………………………………………………………………… | [7 empty] | X
d. Were all underground valves accessible?…………………………………………………………………… | [7 empty] | X
3. WATER SUPPLIES (See Item 15)
a. Was a water flow test of main drain made at the sprinkler riser?………………………………………… | [7 empty] | X
4. TANKS, PUMPS, FIRE DEPARTMENT CONNECTIONS
a. Are fire pumps, gravity tanks, reservoirs and pressure tanks in good condition and properly maintained? | [8 empty] | X
b. Are fire dept connections in satisfactory condition, couplings free, caps in place, and check valves tight? | [9 empty] | X
c. Are they accessible and visible?………………………………………………………………………………… | [7 empty] | X
5. WET SYSTEMS
a. Are cold weather valves (O.S.&Y.) in the appropriate open or closed position?………………… | [8 empty] | X
b. Have antifreeze system solutions been tested?……………………………………………… | [8 empty] | X
c. Were the antifreeze test results satisfactory?……………………………………………………… | [8 empty] | X
d. Antifreeze Solution FREEZING POINT =
| F' |  | F' |  | F' |  | F'
e. Location of antifreeze systems?
Remarks:
6. DRY SYSTEMS (See Item 10 to 13)
a. Is the dry valve in service?…………………………………………………………………………………………. | [8 empty] | X
b. Are the air pressure and priming water level in accordance with the manufacture's instructions?… | [8 empty] | X
c. Has the operation of the air or nitrogen supply been tested?…………………………………………………… | [8 empty] | X
d. Is the air or nitrogen supply in service?…………………………………………………………………………… | [8 empty] | X
e. Were low points drained during this inspection?………………………………………………………………… | [8 empty] | X
f. Did quick-opening devices operate satisfactorily?………………………………………………………………. | [8 empty] | X
g. Did the dry valve trip properly during the trip pressure test?………………………………………………….. | [8 empty] | X
h. Did the heating equipment in the dry-pipe valve room operate at the time of inspection?…………………… | [8 empty] | X
I. Has oil been checked in air compressor?…………………………………………………………………………. | [8 empty] | X
j. Has condensation been drained from air compressor tank?……………………………………………………. | [8 empty] | X
7. SPECIAL SYSTEMS - as defined in Section 1-3 (See Item 14) | [7 empty] | YES | N/A | NO
a. Did the deluge or pre-action valves operate properly during testing?…………………………………………. | [8 empty] | X
b. Did the heat-responsive devices operate properly during testing?……………………………………………. | [8 empty] | X
c. Did the supervisory devices operate during testing?…………………………………………………………… | [8 empty] | X
8. ALARMS
a. Did the water motor and gong test satisfactorily?………………………………………………………………. | [8 empty] | X
b. Did electric alarm test satisfactorily?…………………………………………………………………………….. | [7 empty] | X
c. Did supervisory devices operate during testing?………………………………………………………………. | [7 empty] | X
d. Monitoring Co. |  | Moutain Alarm |  |  |  | Code
9. SPRINKLERS
a. Are all sprinklers free from corrosion, loading or obstruction to spray discharge?…………………………. | [7 empty] | X
b. Are sprinklers less than 50 years old? (Sample testing required after 50 years)…………………………… | [7 empty] | X
c. Is stock of spare sprinklers available?…………………………………………………………………………… | [7 empty] | X
d. Is spare head wrench available?…………………………………………………………………………………. | [9 empty] | X
e. Does the exterior condition of sprinkler system appear to be satisfactory?…………………………………. | [9 empty] | X
f. Temperature. Are sprinklers of proper temperature ratings for their locations?…………………………….. | [7 empty] | X
10. Date Dry-Pipe Valve trip tested (control valve partially open)*………………………………………………. | [8 empty] | X
11. Date Dry-Pipe Valve trip tested (control valve fully open)*………………………………………………….. | [8 empty] | X
12. Date quick-opening devices tested*……………………………………………………………………………. | [8 empty] | X
13. Date Deluge or Pre-action Valve tested*………………………………………………………………………. | [8 empty] | X
*See Trip Test Table which follows.
TRIP TEST TABLE
|  | Dry Valve |  |  | Quick opening device
| Make | Model | Serial # |  | Make | Model | Serial #
DRY PIPE
OPERATING | Air Compressor | Time to trip |  | Water | Air | Trip Point | Time water reached | Alarm operated
TEST | On: | thru test pipe |  | Pressure | Pressure | Air Pressure | test outlet | properly?
| Off: | Minutes | Seconds | PSI | PSI | PSI | Min Sec. | Yes | No
Without QOD
N/A | With QOD
If no, explain:
Operation: Pneumatic Electric Hydraulic
| Piping supervised? Yes No |  |  |  | Detecting media supervised? Yes No
Does valve operate from the manual trip and /or remote control station? Yes No
DELUGE & | Is there an accessible facility in each circuit station? |  |  |  |  | If no, explain:
PREACTION |  | Yes | No
VALVE | Make | Model | Does each circuit operate |  |  | Does each circuit |  | Maximum time to
|  |  | supervision loss alarm? |  |  | operate valve release? |  | operate release?
N/A |  |  | Yes | No |  | Yes | No | Min. | Sec.
14. SPECIAL SYSTEMS
Control Valves |  | Number | Type |  | Open | Secured | Closed | Signs | Exercised
City connection control valves |  | 1 | GATE |  |  |  |  | X | X
Tank control valves
Pump control valves
Sectional control valves
System control valves |  | 2 | BFV |  | X | X | X | X | X
Other control valves
15. EQUIPMENT
a. Make & model number of sprinkler valve: |  |  |  | Ames 2000B 1 1/4" inch DC
b. Type of heads: |  | V2708 155° white pendant, TY3131 155° brass upright
c. Type of canopies: |  | Concealer White
16. MAIN DRAIN TEST AT SPRINKLER RISER
Water supply source |  | City | X | Tank |  | Pump |  | PSI |  | N/A
Last water | Date | Test pipe location |  | Size Test Pipe |  | Initial Pressure | Static Pressure | Residual Pressure
Flow test
This water | Date | Test pipe location |  | Size Test Pipe |  | Initial Pressure | Static Pressure | Residual Pressure
Flow test | 2013-10-25 | Riser |  | 1 1/4" inch |  | 110 | 110 | 105
a. Did water pressure return to normal with in 90 seconds?......................................................................... | [7 empty] | X | Pass |  | Fail
17. Explain any "NO" answers & comments: |  |  |  | No spare head wrench in spare head box. Alarm pane, dialer trouble, silence and
reset buttons do not respond. West vestibule, no coverage in, recommend adding one (1) pendant head.
18. Adjustments or corrections made during this inspection:
19. Although these comments are not the result of an engineering review, the following desirable improvements are recommended:
Signature: | Heath Dangerfield | [5 empty] | Date: | 2013-10-25
Utah State License Number: |  | 61931